## Main
Temperatures | Note (1) |  |  | Location = | Tuscaloosa
Winter Outdoor | to | 20 | ºF |  |  |  | Floor Area | Aflr | 1400 | sq. ft.
Winter Indoor | ti | 70 | ºF |  |  |  | Avg. Height | CeilHt | 8 | ft.
Sum. Outdoor | todb | 95 | ºF | Sp. Hum. | #VALUE! | Lbw/Lba | Building | Leakage | 3 | Tight = 1 | Medium=2 | Loose =3
| towb | 75 | ºF | Rel. Hum. | #VALUE! | % | Elevation (1) | Elev | 170 | ft
Sum. Indoor | tidb | 75 | ºF | Sp. Hum. | #VALUE! | Lbw/Lba | Latitude (1) | Lat | 32 | ºN
| tiwb | 63 | ºF | Rel. Hum. | #VALUE! | %
Daily Range | DR | 20 | ºF
Sens. Heat Ratio | SHR | 0.7 | Note( 2) |  | Zone 1 |  |  | Zone 2
Windows | U (4) | SC (4) | GLF (5) | Area (sf) | qc (MBtu/h) | qh(MBtu/h) | Area (sf) | qc (MBtu/h) | qh(MBtu/h)
North | 0.55 | 0.55 | 24.625 | 14 | 0.34475 | 0.385
NE | 0.55 | 0.55 | 40.25 |  | 0 | 0
East | 0.55 | 0.55 | 54 | 40 | 2.16 | 1.1
SE | 0.55 | 0.55 | 45.7 |  | 0 | 0
South | 0.55 | 0.55 | 30.075 | 14 | 0.42105 | 0.385
SW | 0.55 | 0.55 | 45.7 |  | 0 | 0
West | 0.55 | 0.3 | 34.4545 | 64 | 2.2051 | 1.76
NW | 0.55 | 0.55 | 40.25 |  | 0 | 0
Horz. | 0.55 | 0.55 | 90.875 |  | 0 | 0
Walls | U |  | CLTD (6)
North | 0.055 |  | 13 | 210 | 0.15015 | 0.5775
NE | 0.055 |  | 19 |  | 0 | 0
East | 0.055 |  | 23 | 340 | 0.4301 | 0.935
SE | 0.055 |  | 21 |  | 0 | 0
South | 0.055 |  | 16 | 210 | 0.1848 | 0.5775
SW | 0.055 |  | 21 |  | 0 | 0
West | 0.055 |  | 23 | 316 | 0.39974 | 0.869
NW | 0.055 |  | 19 |  | 0 | 0
Doors | U |  | CLTD (6)
North | 0.25 |  | 13 |  | 0 | 0
NE | 0.25 |  | 19 |  | 0 | 0
East | 0.25 |  | 23 | 20 | 0.115 | 0.25
SE | 0.25 |  | 21 |  | 0 | 0
South | 0.25 |  | 16 |  | 0 | 0
SW | 0.25 |  | 21 |  | 0 | 0
West | 0.25 |  | 23 | 20 | 0.115 | 0.25
NW | 0.25 |  | 19 |  | 0 | 0
Roof/Ceiling | U |  | CLTD (6)
Roof 1 | 0.033 |  | 47 | 1400 | 2.1714 | 2.31
Roof 2 |  |  |  |  | 0 | 0
Partition | U |  | CLTD (6)
(To Unc. Space) |  |  | 12 |  | 0 | 0
Crawl Space | U |  | CLTD (6)
(or floor garage) |  |  | 12 |  | 0 | 0
Slab | R (ins) | UP | CLTD (7) | Perimeter
|  | 0.5 |  | 156 |  | 3.9
Infiltration | ACH | Vol | cfm
Winter | #VALUE! | 11200 | #VALUE! |  |  | #VALUE!
Summer | #VALUE! | 11200 | #VALUE! |  | #VALUE!
People | Number |  | Btu/h-per
| 5 |  | 230 |  | 1.15
Internal (AVG) | Btu/h | Watts
Kitchen/Laundry | 1600 |  |  |  | 1.6
Other (in watts) |  | 400 |  |  | 1.3648
Sensible
Cool Subtotal | MBtu/h |  |  |  | #VALUE!
Heat Subtotal | MBtu/h |  |  |  |  | #VALUE!
| Clg.Fac | Htg.Fac
Duct | 0.1 | 0.1 |  |  | #VALUE! | #VALUE!
Sensible
Cool Total | MBtu/h |  |  |  | #VALUE!
Heat Total | MBtu/h |  |  |  |  | #VALUE!
Net Total
Cooling | MBtu/h |  |  |  | #VALUE!
Heating | MBtu/h |  |  |  |  | #VALUE!
Residential Heating and Cooling Load Calculation - 2001 ASHRAE Fundamentals Handbook
(Implemented by Dr. Steve Kavanaugh)

## Duct
| Insulation | Cooling | Gains | Heating | Losses
Duct Location | (hr-ft-F/Btu) | Supply | Return | Supply<120 F | Supply>120 F | Return
Outdoors, open to well vented | None | 0.25 | 0.15 | 0.25 | 0.3 | 0.15
space, uninsulated, | R2 | 0.15 | 0.08 | 0.15 | 0.2 | 0.08
unconditioned space | R4 | 0.1 | 0.06 | 0.1 | 0.15 | 0.06
| R6 | 0.05 | 0.03 | 0.05 | 0.1 | 0.03
Ducts located in enclosed, | None | 0.2 | 0.12 | 0.2 | 0.25 | 0.12
insulated, unconditioned, | R2 | 0.1 | 0.06 | 0.1 | 0.15 | 0.06
unvented spaces | R4 | 0.05 | 0.03 | 0.05 | 0.1 | 0.03
| R6 | 0.03 | 0 | 0.03 | 0.05 | 0
| None | 0.1 | 0 | 0.1 | 0.15 | 0
Ducts located in return air | R2 | 0.05 | 0 | 0.05 | 0.1 | 0
ceiling plenum | R4 | 0.03 | 0 | 0.03 | 0.08 | 0
| R6 | 0 | 0 | 0 | 0.03 | 0
| None | 0.1 | 0.06 | 0.1 | 0.15 | 0.06
Ducts buried in or under | R2 | 0.05 | 0.03 | 0.05 | 0.1 | 0.03
concrete slab | R4 | 0.03 | 0 | 0.03 | 0.08 | 0
| R6 | 0 | 0 | 0 | 0.03 | 0
Ducts in conditioned space or |  | 0 | 0 | 0 | 0 | 0
stubbed up in space, short run | Any | 0 | 0 | 0 | 0 | 0
Cooling
Factor
Heating Factors

## ASHRAE Table 5
Table 5 - Shading Coefficients and U-Factors for Residential Windows
| None |  | Drapes, Venetian Blind, or Translucent Roller Shade |  | Opaque Roller Shade
Glass Type | SC | U | SC | U | SC | U
Single | 1 | 1.04 | 0.5 | 0.81 | 0.38 | 0.81
Double | 0.88 | 0.61 | 0.45 | 0.55 | 0.36 | 0.55
Heat Absorbing | 0.58 | 0.45 | 0.37 | 0.44 | 0.33 | 0.44
Triple | 0.8 | 0.44 | 0.44 | 0.4 | 0.36 | 0.4
Source: ASHRAE Manual - 2001 Fundamentals, The American Society of Heating, Refrigeration and Air Conditioning Engineers

## Notes
Notes
1 | Weather and climatic information available Table 1A & 1B, Chp. 27, 2001 ASHRAE Fundamental Handbook.
2 | SHR = Sensible Load/Total Load Use: 0.65 for Tropic, 0.70 Humid, 0.75 Avg., 0.80 Dry, 0.85 Arid
3 | Values curve fit fromTables 7 & 8, Chp. 28, 2001 ASHRAE Fundamental Handbook.
4 | See Table 5, Chp. 28, 2001 ASHRAE Fundamental Handbook (reproduced ona another worksheet).
5 | Values curve fit from Table 3, Chp. 28, 2001 ASHRAE Fundamental Handbook.
6 | Values curve fit from Table 1, Chp. 28, 2001 ASHRAE Fundamental Handbook.
7 | See Table 16, Chp. 28, 2001 ASHRAE Fundamental Handbook.